# TECHNICAL DATA SHEET

| Power transformer Ungheni 25 MVA, 115 ± 9x1.78 % /38.5±2x2.5%/11 kV |  |  |  |  |
| --- | --- | --- | --- | --- |
| No | Description | Unit | Data required | Data offered |
| 1 | GENERAL |  |  |  |
|  | Manufacturer |  |  |  |
|  | - country |  |  |  |
|  | - city |  |  |  |
|  | Kind of installation |  | outdoor |  |
|  | Standards |  | IEC60076 |  |
|  |  |  | IEC60137 |  |
|  |  |  | IEC61463 |  |
|  |  |  | IEEE 693-2005 |  |
|  | Single or three-phase unit |  | Three-phase |  |
|  | Type of core |  | 3 limb, step-lap stacked core form |  |
|  | Type of tank |  | Upper flange tank |  |
|  | Tank fully vacuum proof |  | Yes |  |
|  | Number of windings |  | Three |  |
|  | Winding material (HV,MV,LV) |  | Coper |  |
|  | Insulation oil |  |  |  |
|  | - manufacturer |  |  |  |
|  | - type |  |  |  |
|  | - specification of oil |  | IEC 60296 |  |
|  | - insulation oil inhibited |  | Yes |  |
|  | - test method for corrosive sulphur |  | IEC 62535 and ASTDM D1275B |  |
| 2 | RATINGS |  |  |  |
|  | Rated power at nominal voltage (primary/secondary/tertiary) |  |  |  |
|  | - at ONAN cooling | MVA | 20/20/20 |  |
|  | - at ONAF cooling | MVA | 25/25/25 |  |
|  | Maximum ambient temperature | ⁰C | 50 |  |
|  | Annual average ambient temperature | ⁰C | 15 |  |
|  | Minimum ambient temparature | ⁰C | -30 |  |
|  | Maximum service altitude | m | 1000 |  |
|  | Temperature rise limits at all tap changer settings |  |  |  |
|  | - oil/top | K | 50 |  |
|  | - windings/average | K | 55 |  |
|  | - windings/hot spot | K | 68 |  |
|  | Rated voltages (no load) |  |  |  |
|  | - HV | kV | 115 |  |
|  | - MV | kV | 38.5 |  |
|  | - LV | kV | 11 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Permissible load at neutral point | % | solidly earthed/surge arrester |  |
|  | Vector group symbol |  | YNyn0d11 |  |
|  | Impedance voltage – HV/LV (25 MVA basis) |  |  |  |
|  | - maximum tap position | % | Specify |  |
|  | - nominal tap position | % | 17.5 |  |
|  | - minimum tap position | % | Specify |  |
|  | Impedance voltage – HV/MV (25 MVA basis) |  |  |  |
|  | - maximum tap position | % | Specify |  |
|  | - nominal tap position | % | 10.5 |  |
|  | - minimum tap position | % | Specify |  |
|  | Impedance voltage – secondary/tertiary (25 MVA basis) | % | Min. 6.5 (±30%/-0%) |  |
|  | Magnetic flux density at |  |  |  |
|  | -rated voltage and frequency | Tesla | Max. 1.7 |  |
|  | No load losses (tolerance +0%) | kW | ˂15 |  |
|  | No load current (Io/In) | % | 0.1 |  |
|  | Core losses (W17/50) | W/kg | Max. 0.9 |  |
|  | Short circuit voltage |  |  |  |
|  | - HV-LV | % | 17.5 |  |
|  | - HV-MV | % | 10.5 |  |
|  | - MV-LV | % | 6.5 |  |
|  | Load losses at rated power |  |  |  |
|  | HV/LV (25 MVA basis) |  |  |  |
|  | - maximum tap position | kW | Specify |  |
|  | - nominal tap position | kW | Specify |  |
|  | - minimum tap position | kW | Specify |  |
|  | HV/MV (25 MVA basis) |  |  |  |
|  | - maximum tap position | kW | Specify |  |
|  | - nominal tap position | kW | Specify |  |
|  | - minimum tap position | kW | Specify |  |
|  | MT/JT (25 MVA basis) | kW | Specify |  |
|  | HV winding (25 MVA basis) |  |  |  |
|  | - maximum tap position | kW | Specify |  |
|  | - nominal tap position | kW | Specify |  |
|  | - minimum tap position | kW | Specify |  |
|  | LV winding (25 MVA basis) | kW | Specify |  |
|  | MT winding (25 MVA basis) |  |  |  |
|  | - maximum tap position | kW | Specify |  |
|  | - nominal tap position | kW | Specify |  |
|  | - minimum tap position | kW | Specify |  |
|  | Power consumption of cooling plant | kW | Specify |  |
|  | Efficiency referred to 75 ⁰C at rated voltage taping and at: |  |  |  |
|  | - 100% rated output and 1.0 power factor | % | 99.7 |  |
|  | - 75% rated output and 1.0 power factor | % | Specify |  |
|  | - 50% rated output and 1.0 power factor | % | Specify |  |
|  | - 25% rated output and 1.0 power factor | % | Specify |  |
|  | - 100% rated output and 0.8 power factor | % | Specify |  |
|  | - 75% rated output and 0.8 power factor | % | Specify |  |
|  | - 50% rated output and 0.8 power factor | % | Specify |  |
|  | - 25% rated output and 0.8 power factor | % | Specify |  |
|  | Voltage variation range HV | kV | +/- 18.423 |  |
|  | Taping range HV | % | +/- 16 |  |
|  | Number of steps HV | steps | +/- 9 |  |
|  | Continuous power on all taps |  | Yes |  |
|  | Voltage variation range MV 38.5 kV | kV | +/- 1.925 |  |
|  | Tapping range MV 38.5 kV | % | +/- 5 |  |
|  | Number of steps MV 38.5 kV | steps | +/- 2 |  |
|  | Principal taping HV | kV | 115 |  |
|  | Principal taping MV | kV | 38.5 |  |
|  | Winding insulation design |  |  |  |
|  | - HV |  | Uniform |  |
|  | - MV |  | Uniform |  |
|  | - LV |  | Uniform |  |
|  | Seismicity on MSK scale |  | IX |  |
| 3 | INSULATION LEVEL |  |  |  |
|  | Insulation level HV winding |  |  |  |
|  | - Power frequency withstand voltage line/neutral | kV | 230/230 |  |
|  | - Lightning impulse level line/neutral | kV | 550/550 |  |
|  | Insulation level LV winding |  |  |  |
|  | - Power frequency withstand voltage | kV | 34 |  |
|  | - Lightning impulse level | kV | 110 |  |
|  | Insulation level MT winding |  |  |  |
|  | - Power frequency withstand voltage line/neutral | kV | 95/95 |  |
|  | - Lightning impulse level line/neutral | kV | 250/250 |  |
| 4 | OPERATION DETAILS |  |  |  |
|  | Cooling method |  | ONAF |  |
|  | Noise level (LpA) at a measuring distance of 2.0 m (all forced cooling in operation) | dB(A) | Max. 60 |  |
| 5 | BUSHINGS |  |  |  |
|  | HV (lines) |  |  |  |
|  | - manufacturer |  |  |  |
|  | - type |  |  |  |
|  | - rated current | A | 800 |  |
|  | - power frequency test voltage | kV | 255 |  |
|  | - lightning impulse level |  | 550 |  |
|  | - minimum creepage distance in accordance with IEC 60815 | mm | 2835 |  |
|  | - cantilever load level according to IEC 60137 | daN | Specify |  |
|  | HV (neutral) |  |  |  |
|  | - manufacturer |  |  |  |
|  | - type |  |  |  |
|  | - rated current | A |  |  |
|  | - power frequency test voltage | kV | 105 |  |
|  | - lightning impulse level |  | 250 |  |
|  | - minimum creepage distance in accordance with IEC 60815 | mm | 1050 |  |
|  | - cantilever load level according to IEC 60137 | daN | Specify |  |
|  | LV |  |  |  |
|  | - manufacturer |  |  |  |
|  | - type |  |  |  |
|  | - rated current | A | 2000 |  |
|  | - power frequency test voltage | kV | 42 |  |
|  | - lightning impulse level |  | 110 |  |
|  | - minimum creepage distance in accordance with IEC 60815 | mm | 280 |  |
|  | - cantilever load level according to IEC 60137 | daN | Specify |  |
|  | MT (lines/neutral) |  |  |  |
|  | - manufacturer |  |  |  |
|  | - type |  |  |  |
|  | - rated current | A | 630 |  |
|  | - power frequency test voltage | kV | 105 |  |
|  | - lightning impulse level |  | 250 |  |
|  | - minimum creepage distance in accordance with IEC 60815 | mm | 1050 |  |
|  | - cantilever load level according to IEC 60137 | dan | Specify |  |
| 6 | CURRENT TRANSFORMERS |  |  |  |
|  | 115 kV line side |  |  |  |
|  | For protection purposes |  |  |  |
|  | Rated output | VA | 30 |  |
|  | Ratio |  |  |  |
|  | - primary | A | 150-300 |  |
|  | - secondary | A | 5 |  |
|  | Class |  | 5P20 |  |
|  | For protection purposes |  |  |  |
|  | Rated output | VA | 30 |  |
|  | Ratio |  |  |  |
|  | - primary | A | 150-300 |  |
|  | - secondary | A | 5 |  |
|  | Class |  | 5P20 |  |
|  | 115 kV neutral side |  |  |  |
|  | For protection purposes |  |  |  |
|  | Rated output | VA | 10 |  |
|  | Ratio |  |  |  |
|  | - primary | A | 150-300 |  |
|  | - secondary | A | 5 |  |
|  | Class |  | 5P20 |  |
|  | 38.5 kV line side |  |  |  |
|  | For protection purposes |  |  |  |
|  | Rated output | VA | 30 |  |
|  | Ratio |  |  |  |
|  | - primary | A | 600-800 |  |
|  | - secondary | A | 5 |  |
|  | Class |  | 5P20 |  |
|  | For protection purposes |  |  |  |
|  | Rated output | VA | 30 |  |
|  | Ratio |  |  |  |
|  | - primary | A | 600-800 |  |
|  | - secondary | A | 5 |  |
|  | Class |  | 5P20 |  |
| 7 | ON-LOAD TAP CHANGER |  |  |  |
|  | Manufacturer |  |  |  |
|  | Type |  |  |  |
|  | Rated through current | A | ≥400 |  |
|  | Rated step capacity | kVA | ≥2200 |  |
|  | Lightning impulses level | kV | 550 |  |
|  | Power frequency withstand test voltage | kV | 230 |  |
|  | Rated step voltage per phase | kV | 3200 |  |
|  | Short-time current |  |  |  |
|  | - 3s value | kA | ≥10 |  |
|  | - peak value | kA | ≥25 |  |
|  | Type of connection |  | Neutral |  |
|  | Type of switching |  | Vacuum type diverter switch |  |
|  | Contact life operation | Nos | Min. 500 000 |  |
|  | Number of switching operation till first revision | Nos | Min. 250 000 |  |
|  | Auxiliary supply voltage (AC) | V | 400/230 |  |
| 8 | PROTECTION AND MONITORING EQUIPMENT |  |  |  |
|  | - Buchholz relay |  | EMB BF 80/10 (or. equ.) |  |
|  | - Oil flow operated protection relay |  | EMB URF 25/10 (or. equ.) |  |
|  | - Conservator gas detection relay |  | EMB CF-38 (or/ equ.) |  |
|  | - Oil level indicator |  |  |  |
|  | Type |  |  |  |
|  | Manufacturer |  |  |  |
|  | - Pressure relief device |  | resettable spring loaded |  |
|  | Type |  |  |  |
|  | Manufacturer |  |  |  |
|  | - Dehydrating breather |  | Automatic, maintenance free |  |
|  | Type |  |  |  |
|  | Manufacturer |  |  |  |
|  | - Oil temperature indicator |  |  |  |
|  | Type |  |  |  |
|  | Manufacturer |  |  |  |
|  | - Winding temperature indicator |  |  |  |
|  | Type |  |  |  |
|  | Manufacturer |  |  |  |
| 9 | MASSES, MEASURES AND DRAWINGS |  |  |  |
|  | Transformer masses: |  |  |  |
|  | - total mass | kg |  |  |
|  | - transportation mass | kg |  |  |
|  | - untanking mass | kg |  |  |
|  | - mass of insulating liquid | kg |  |  |
|  | Overall dimensions including bushings: |  |  |  |
|  | - height | mm |  |  |
|  | - depth | mm |  |  |
|  | - width | mm | max. 6250 |  |
|  | Gauge of the tank |  |  |  |
|  | - longitudinal | mm | 1524 |  |
|  | - transverse | mm | 2000 |  |
| 10 | RELIABILITY REQUIREMENTS |  |  |  |
|  | Design of windings and/or magnetic core pressing system shoud not require any maintenance for the whole expected life term |  | Yes |  |
|  | Manufacture has to have experience in short-circuit tests ≥ 110 kV rated voltage transformers (withstand short circuit) according to IEC standard in independent laboratories not earlier than 2010 |  | Specify transformer type, present test report |  |
|  | Life time | year | Min. 30 |  |
| 11 | DELIVERY |  |  |  |
|  | Incoterms |  | DAP |  |
|  | Unloading on site |  | No |  |
| 12 | DOCUMENTS TO BE PROVIDED WITH THE OFFER |  |  |  |
|  | Transformer data plate (photo or drawing) |  | Provide |  |
|  | Passport or Test Certificate of the similar* transformer previously manufactured not earlier than 2010 |  | Provide |  |
|  | Reference list of the similar transformers for the last 5 years with end users contacts |  | Provide |  |
|  | Certificate for manufacture’s test laboratory (ISO/IEC) |  | Provide |  |
|  | Outline transformer drawing |  | Provide |  |
|  | Oil test certificate |  | Provide |  |
|  | Short-circuit test report |  | Provide |  |
|  | OLTC Type Test Report performed in independent and accredited European Laboratory according to IEC 60214-I:2014, |  | Provide |  |
|  | OLTC instalatuon and operation manual |  | Provide |  |
|  | Other documents required according to chapter 5 of the present document |  | Provide |  |

- Similar transformer is a three – winding transformer with same/similar rated power, HV / MV/LV rated voltage, no-load and load losses, impedance voltage, sound pressure level.

- Bidder’s name: ___________________

- Signature and stamp/electronic signature of the bidder:___________________________