## UPS and Air-cooling systems
Item | Part name | Specifications |  | Q-ty | Unit price | Total price
Lot1
1 | UPS 15-20 kVA | 1.1 General UPS requirements: |  | 2 units
|  | UPS Topology | Tip On-line double conversion according CEI EN 62040-3 VFI-SS-111
|  | > 150%, 200ms | For installation on IT Rack
|  | UPS output power | 11-15-20 kVA (SW upgradable)
|  | Nominal input voltage | 380V/400V/415V
|  | Input voltage range without battery discharge depending on load % | 173-498 V
|  | Nominal input frequency | 50/60 Hz
|  | Input frequency range | 40-70 Hz
|  | Input power factor at full load (kw/kva) | 0,99
|  | THD at full linear load (THDI%) | ≤3 %
|  | Nominal output voltage | 380/400/415 or 220/230/240 V selectable at installation
|  | Inverter overload capacity at 25°C | 105% for 60 min; 125% 5min; 150% for 1 min, > 150%, 200ms
|  | Double conversion efficiency | 96.2%
|  | ECO Mode Efficiency | 99%
|  | By-pass voltage tolerance | -50
|  | By-pass frequency tolerance | +/-10%
|  | Battery blocks per string | 24-40
|  | Battery charger min. current | 12 A
|  | Parallel connection of UPS | Up to 4 units
|  | Noise at 1 m (dBA) | ≤59 dBa
|  | Ventilation | Face to back
|  | Protection IEC (60529) | IP20
1.2 UPS configuration:
|  | UPS back-up time at 100% load 12 KW and PF =1 | 8 min.
|  | Battery type/service life | AGM/10 years
|  | Battery voltage temperature compensation kit | Included
|  | Room temperature and relative humidity sensor | Included
|  | Ethernet interface for monitoring | Protocol SNMP
|  | Sliding kit for UPS and battery | YES
|  | By-pass | Electronic and Manual
|  | Input POD | Protection CB/Input/ Output/ Battery, By-pass switch
|  | Load power distribution | YES
|  | Rack/Tower design delivered with rack mount: UPS/ input POD/ Load distribution dimension/Battery sets accessories | 3U/3U/3U/6U(4U)
|  | General standards | EN/IEC/AS 62040-1, EN/IEC/AS 62040-2, CEI EN 62040-3 VFI-SS-111
1.3 Requirements to supplier:
Status of official distributor and service center of manufacturer in Republic of Moldova
Copy of engineer certificate for installation, maintenance and repair of offered type equipment’s
SLA 24/24
Stock of replacement spares
Installation services and materials included in the offer
Warranty – min. 24 months from installation date
1.4 Delivery and payment conditions:
Delivery time: 4 weeks (after receiving 50% pre-payment)
Delivery address: 78, 31 August 1989 str. Chisinau, Republic of Moldova, of. 310a
Payment terms: 50% pre-payment and 50% final payment after delivery and acceptance of goods (payment conditions specified in the commercial contract)
Price should be given excluding VAT
Lot 2
1 | First Cooling Unit: 14kW | 1.1 General cooling unit requirements: |  | 1 unit
|  | Cooling principle | Direct expansion
|  | Expansion device | Thermostatic valve
|  | Refrigerant | R407C or analogous
|  | Mounting of indoor unit | Ceiling mounting
|  | Mounting of outdoor unit | Wall or Floor
|  | Main power supply | 400/3N/50 (or similar)
|  | Compressor type/quantity | scroll / 1 or analogous
|  | Piping length from indoor to outdoor unit | Max. 50 m
|  | Vertical distance | Max 20 m
|  | Operation temperature limits | -30/+50°С
|  | Condenser fan | Variable speed
1.2 Cooling unit configuration:
|  | Total cooling capacity | 14 KW
|  | Indoor unit airflow | Cold air direction vertical from top to bottom
Hot air aspiration horizontal from selling level
|  | Outdoor sound pressure level | Not more than 58 dBa
|  | Indoor sound pressure level | ~ 63 dBa
|  | Protection switches | Low and High pressure
|  | Temperature setpoint | 23
|  | Filter type/Efficiency | Pleated/G4 or analogous
|  | Clogged filter pressure switch | Yes
|  | Free-cooling option | Yes / direct free cooling
|  | Ethernet interface for monitoring | Protocol SNMP
|  | Display | Yes
|  | Dry contacts | Yes
|  | Fan type | EC
|  | Filter spare | yes
1.3 Requirements to supplier:
Status of official distributor and service center of manufacturer in Republic of Moldova
Copy of engineer certificate for installation, maintenance and repair of offered type equipment’s
SLA 24/24
Stock of replacement spares
Installation services and materials included in the offer(Need to intergrade with existing HVAC systems)
Warranty – min. 24 months from installation date
1.4 Delivery and payment conditions:
Delivery time: 4 weeks (after receiving 50% pre-payment)
Delivery address: 78, 31 August 1989 str. Chisinau, Republic of Moldova, of. 310a
Payment terms: 50% pre-payment and 50% final payment after delivery and acceptance of goods (payment conditions specified in the commercial contract)
Price should be given excluding VAT
Total price